## Sheet1
UPFLOW ANAEROBIC SLUDGE BLANKET (UASB) DESIGN CALCULATIONS - SI UNITS
Instructions for use: Enter Values in Yellow Box.
1. User Input
a) Wastewater Characteristics
Influent Flow rate, Qavg = |  |  | 10000 | m3/d |  |  |  | Influent TSS = | 395 | mg/L
Influent COD = |  |  | 820 | mg/L |  |  |  | Influent VSS = | 270 | mg/L
Influent BOD = |  |  | 350 | mg/L |  |  |  | Sulphate = | 105 | mg/L
Temperature Ti = |  |  | 27 | °C | (Temperature Range of 20° to 28°C)
b) Coefficients and Design Parameters
|  |  | BOD removal efficiency fraction = |  |  | 0.8
|  |  | Residual Biomass fraction = |  |  | 0.1 | (g VSS cell/g VSS BOD decay)
|  |  | Non-degradable residue fraction = |  |  | 0.6
|  |  | Depth of sludge blanket = |  |  | 2.2 | m
|  |  | Effectiveness coefficient in SRT value = |  |  | 0.85
|  |  | Avg. concentration of sludge in blanket = |  |  | 70 | kg/m3
|  |  | Overall depth of reactor required = |  |  | 5 | m
|  |  | COD removal efficiency fraction = |  |  | 0.8
|  |  | Sulphate removal efficiency fraction = |  |  | 0.8
|  |  | Methane production at 0°C = |  |  | 0.35 | m3/kg COD (std.)
2. Calculations (done by the spreadsheet)
a) Sludge Production
| VSS produced in BOD removal = |  |  | 28 | mg/L
| Non-degradable residue = |  |  | 162 | mg/L
| Ash received in inflow = |  |  | 125 | mg/L
| Total Sludge produced = |  |  | 315 | mg/L
b) Calculation of SRT and HRT values
| Solids Retention Time, SRT = |  |  | 30 | days
(enter an initial estimate)
| Calculated Hydraulic Ret. Time, HRT = |  |  | 8.66 | hrs at avg. flow
|  |  |  | 4.33 | hrs at peak flow
c) Calculations of Upflow Velocity
| Upflow velocity at avg. flow = |  |  | 0.577 | m/hr
Upflow Velocity in consideration with retaining Flocculent sludge within UASB =
|  |  |  | 0.5 | m/hr
| Upflow Velocity at peak flow = |  |  | 1 | m/hr | OK
d) Calculations of Reactor Dimensions
|  | Reactor area Required = |  | 833 | m2
|  | Reactor width = |  | 24 | m
|  | Reactor Length = |  | 35 | m
|  | Total Reactor Height = |  | 5.5 | m (with 0.5m Freeboard)
Check For Organic Loading
| Volumetric Organic loading = |  |  | 1.95 | kg COD/m3/d
| Organic loading on sludge blanket = |  |  | 0.106 | kg COD/kg VSS/d
e) COD Removed and Methane Produced
| Total COD removed = |  |  | 6,560 | kg/d
| COD consumed in Sulphate reduction = |  |  | 562.8 | kg/d
| Total methane produced at Ti /day = |  |  | 2,306.50 | m3/d
| Methane leaving as dissolved in effluent = |  |  | 280 | m3/d
| Usable Methane = |  |  | 0.309 | m3/kg COD